# 2.  Installation

Before installing the EXM-PS, unpack and inspect it for shipping damage.

*	do not remove the module from its anti-static bag unless you are in a static-free environment.  the exm-ps, like most other electronic devices, is susceptible to esd damage.  esd damage is not always immediately obvious, in that it can cause a partial breakdown in semiconductor devices that might not immediately result in a failure.

*	ensure that the installation process as described herein is also performed in a static-free environment.

## Safety

Please take a moment to review these safety precautions.  They are provided for your protection and to prevent damage to the module.  This safety information applies to all operator and service personnel.

µ §		The exclamation point within an equilateral triangle is intended to alert the user to the presence of important operating and maintenance instructions in the literature accompanying the product. If you see this symbol on the EXM-PS, be sure to refer to this manual.

µ §	indicates DANGER.  These are safety issues that, if not followed, could result in severe personal injury.

!  	indicates WARNING. These are informational instructions that pertain to proper use and protection of the EXM-PS power module.

µ §	The EXM-PS case is grounded via the front-panel ground connection on the power input terminal strip.  This terminal MUST be connected to ground to prevent a shock hazard in the event of a malfunction of the EXM-PS unit.

µ §	Do not operate this product in an atmosphere of explosive gases. The module provides no explosion protection from static discharge or arcing components.

!	Never apply a voltage higher than the rating shown on the front panel of the 
EXM-PS unit.  Higher voltages may cause the fuse on the EXM-PS to blow, and may cause damage to the power supply circuits.

!	For continued protection against risk of fire, replace fuses with only the same type and ratings.

µ §To lessen the risk of electric shock, the potential between ground and either the + or - inputs should be less than 72 volts.

## Insertion in an EMC Chassis

Insertion of the EXM-PS into an EMC chassis is straightforward.  Make sure the power is not connected to the EXM-PS and that the front panel power switch is off. Remove any blank EXM panel from the chassis (by unscrewing the thumbscrews) and insert the EXM-PS into the card guides.  Firmly press the EXM-PS front panel to ensure that the module is properly seated in the backplane and secure it with the thumbscrews. Tighten with a screwdriver to lessen shock hazard.

*	when inserting the exm, avoid touching the circuit board, and make sure the environment is static-free.

*	insert it with adequate continuous force rather than tapping or hammering on it.

## Power Connector

µ §To attach a power cable to the front-panel power connector, strip back the outer insulation 1 1/2" and separate the individual wires.   Strip the insulation on each individual wire 1/4" - 3/8".  If the power cable has three conductors plus a shield wire, twist the shield wire and the ground wire together before inserting into the connector.  One wire at a time, insert each wire until no bare wire is showing and tighten the holding screw.

Figure 1. Power Connector.

Note:  Only use 14 AWG wire in making connections to the power connector.

Positive and negative inputs are isolated from the chassis ground. Either positive or negative can float to a maximum of 72 VDC as long as the "potential" difference across the two connectors does not exceed the input specification.

The chassis ground connection is also connected to logic ground on the EXM expansion interface.

## Cooling Requirements

The system should be installed so that a minimum of 5" of air space is provided on each of the exposed sides of the chassis holding the EXM-PS.  In no case should the temperature of the heatsink on the EXM-PS be allowed to exceed 100°C.

If you have continued "overtemp" problems, a forced-air fan may be necessary to cool the entire system.