## Slide 1: Intel SSD DC P3700/P3600 Firmware 49 Package (Update instructions)

## Slide 2: Update Package –Rev 49 contents
Update Package Includes:
  BL: 8B1B0128.bin
  Windows Free/Release Driver: 1.0.0.1016, Windows Debug Driver (For BL update/Assert clear): 1.0.0.5010 ;
  Firmware: 8DV10049_signed.bin
  Firmware: 8DV10043_signed.bin
  Configuration Manager: 2.1.2
  NCAT: 1.3.0
  NCAT 1.2.0
  VPD RWE tool (To update VPD contents): 1.6.5.9
  SW license
  Tool’s User Guides
  Binary license
  Universal update package with UpdateMeToQS,bat script which can recognize the FW version of the drive and its health status and proceed accordingly.
FW update process is different for samples with FW36/FW41 and FW43

## Slide 3: Full QS update instructions: Update from FW41/FW36 (part 1)
Step 1 Firmware Update to 0043 version
Use Intel SSD Configuration Manager tool to get your P3700/P3600 drive index:
iSSDCM_win64.exe -drive_list (use this index for all future commands instead of “X”)
Use Intel SSD Configuration Manager tool to update firmware to “0043” revision
    iSSDCM_win64.exe -drive_index X -firmware_update 8DV10043_signed.bin
    Drive may enter BAD_CONTEXT_1015 during this process
    Use NCAT 1.2.0 tool to clear this condition
    NCAT120.exe –drive_index X -lowlevelformat
In order to do FW update on ES2 P3700/P3600 SSD – Intel NVMe Debug driver for Windows* is required! (included in this package)

## Slide 4: Update from FW36/FW41 (part 2)
Step 2 Bootloader Update
Use NCAT 1.2.0 tool to update bootloader to “128” revision
    NCAT120.exe -drive_index X –bootloader_update 8B1B0128.bin
Step 3 Configuration Update
Must use NCAT 1.2.0 tool only to update to FW43 configuration/lightswitch (embedded file)
    NCAT120.exe –drive_index X –update_config
    (Drive will enter NO_CONTEXT_7)
    NCAT120.exe -drive_index X –lowlevelformat

## Slide 5: Update from FW36/FW41 (part 3)
Step 4 Firmware Update to 0049 version
Use Intel SSD Configuration Manager tool to update firmware to “0049” revision
    iSSDCM_win64.exe -drive_index X -firmware_update 8DV10049_signed.bin
  Must use NCAT 1.3.0 tool only to update to latest configuration/lightswitch (embedded file)
    NCAT130.exe –drive_index X –update_config
    Power cycle
Contact your NSG AE support in case of any questions

## Slide 6: Update VPD contents (Generic/Channel)
Should be done after full FW update process
The tool needs to have SMBUS access to the P3700/P3600 VPD page contents
It may not work with some server/client boards. It is recommended to use systems with Intel chipset.
It is required to have only one PCIe drive in the system for correct VPD contents update
To update VPD contents:
Go to “RWE VPD tool” folder
Launch “createAndWriteVPD.bat” batch file

## Slide 7: backup

## Slide 8: Update from FW43 to QS Firmware (0049)
Step 1. Use Intel SSD Configuration Manager tool to get your P3700/P3600 drive index:
1) iSSDCM_win64.exe -drive_list (use this index for all future commands instead of “X”)
Step 2. Use Intel SSD Configuration Manager tool to update firmware to “0049” revision
    2) iSSDCM_win64.exe -drive_index X -firmware_update 8DV10049_signed.bin
  Step 3. Use NCAT 1.3.0 tool only (included in the package) to update the bootloader and latest configuration/lightswitch settings (embedded file)
    3) NCAT.exe -drive_index X –bootloader_update 8B1B0128.bin
    4) NCAT.exe –drive_index X –update_config
    5) Power cycle
In order to do FW update on ES2 P3700/P3600 SSD – Intel NVMe Debug driver for Windows* is required! (included in this package)