## Sheet1
Test Case | Test Name | Test Description | Expected Result | Executing date | Result | Ericsson comments | Yoigo comments
1 | Power Grid Failure in A Supply (Fallo de Red - A) | The Grid Fail is reported as an open circuit by the sensor choosen, configured and cabled for this specific alarm, thus the test consist in trigger the alarm by open the circuit. This is done by unplug one of the 2 cables that are connected to ESC. | Alarm raises in the MO: SDN=0,AlarmPort=ElectricityGridA; | 16/04/2013
2 | Power Grid Failure in B Supply (Fallo de Red - B) | The Grid Fail is reported as an open circuit by the sensor choosen, configured and cabled for this specific alarm, thus the test consist in trigger the alarm by open the circuit. This is done by unplug one of the 2 cables that are connected to ESC. | Alarm raises in the MO: SDN=0,AlarmPort=ElectricityGridB; | 16/04/2013
3 | DC System Major Failure in Supply A (Fallo Mayor equipo DC - A) | DC System Major Failure is reported as an open circuit by the sensor choosen, configured and cabled for this specific alarm, thus the test consist in trigger the alarm by open the circuit. This is done by unplug one of the 2 cables that are connected to ESC. | Alarm raises in the MO: SDN=0,AlarmPort=DCMajorA; | 16/04/2013
4 | DC System Major Failure in Supply B (Fallo Mayor equipo DC - B) | DC System Major Failure is reported as an open circuit by the sensor choosen, configured and cabled for this specific alarm, thus the test consist in trigger the alarm by open the circuit. This is done by unplug one of the 2 cables that are connected to ESC. | Alarm raises in the MO: SDN=0,AlarmPort=DCMajorB; | 16/04/2013
5 | DC System Minor Failure in Supply A (Fallo Menor equipo DC - A) | DC System Minor Failure is reported as an open circuit by the sensor choosen, configured and cabled for this specific alarm, thus the test consist in trigger the alarm by open the circuit. This is done by unplug one of the 2 cables that are connected to ESC. | Alarm raises in the MO: SDN=0,AlarmPort=DCMinorA; | 16/04/2013
6 | DC System Minor Failure in Supply B (Fallo Menor equipo DC - B) | DC System Minor Failure is reported as an open circuit by the sensor choosen, configured and cabled for this specific alarm, thus the test consist in trigger the alarm by open the circuit. This is done by unplug one of the 2 cables that are connected to ESC. | Alarm raises in the MO: SDN=0,AlarmPort=DCMinorB; | 16/04/2013
7 | DC Distributor Failure in Supply A (Fallo de Distribución - A) | DC Distributor Failure is reported as an open circuit by the sensor choosen, configured and cabled for this specific alarm, thus the test consist in trigger the alarm by open the circuit. This is done by unplug one of the 2 cables that are connected to ESC. | Alarm raises in the MO: SDN=0,AlarmPort=DCDistributorA; | 16/04/2013
8 | DC Distributor Failure in Supply B (Fallo de Distribución - B) | DC Distributor Failure is reported as an open circuit by the sensor choosen, configured and cabled for this specific alarm, thus the test consist in trigger the alarm by open the circuit. This is done by unplug one of the 2 cables that are connected to ESC. | Alarm raises in the MO: SDN=0,AlarmPort=DCDistributorB; | 16/04/2013
9 | Battery in Supply A (Interruptor de Bateria - A) | Battery alarm is reported as an open circuit by the sensor choosen, configured and cabled for this specific alarm, thus the test consist in trigger the alarm by open the circuit. This is done by unplug one of the 2 cables that are connected to ESC. | Alarm raises in the MO: SDN=0,AlarmPort=BatteryA; | 16/04/2013
10 | Battery in Supply B (Interruptor de Bateria - B) | Battery alarm is reported as an open circuit by the sensor choosen, configured and cabled for this specific alarm, thus the test consist in trigger the alarm by open the circuit. This is done by unplug one of the 2 cables that are connected to ESC. | Alarm raises in the MO: SDN=0,AlarmPort=BatteryB; | 16/04/2013
11 | High Temperature | The temperature sensor reports the room temperature. In this test it is needed to apply heat directly to the sensor with an external heater. After the temperature increases to the 28 ºC an alarm is raised. * If it is needed there is an option for using an additional thermometer to test that the sensor is correctly reporting the temperature in the room. | Alarm raises in the MO: SDN=0,AnalogInputPort=Temp1…..specificProblem="High level" | 16/04/2013
12 | Low Temperature | The temperature sensor reports the room temperature. In this test it is needed to apply cold directly to the sensor. After the temperature decreases to the 10 ºC an alarm is raised. * If it is needed there is an option for using an additional thermometer to test that the sensor is correctly reporting the temperature in the room. | Alarm raises in the MO: SDN=0,AnalogInputPort=Temp1…..specificProblem="Low level" | 16/04/2013