## Slide 2
Points to Remember
BTS Software should be downloaded locally.
There should not be any Alarm (Hardware/ transmission Alarm)
RSSI Value should be Verified.
Transmission Card should be tight.
All the Connector should Tight properly.
Define the TRX TCH, TRX SIG, OMU SIG and EDAP as per the Abis Plan.
Edge/GPRS should be tested in every Sector.
Voice Call should be Tested on every TRX.
Checking of external alarms at the time of commissioning.
BTS Synchronization should be defined properly.
Make sure to disable all unused LIFs / PIFs.

## Slide 3: Things to be checked Before the Site Commissioning start
Please check the length of the power cable and capacity of the power plant. (Verify the Voltage)
E1 Verification till the BSC ET (There Should not be error on E1)
Feeder VSWR testing and Return Loss (If the VSWR is more than 1.3, it is very important to check the feeder end to end. Also perform cable loss measurements.)
Connect Jumper cable to the NSN BTS Top – Mark the feeders for sector A,B,C
  Make sure to check all the grounding points before inserting the plug in units.
  Connect the power supply and check the input voltage at the connector.
  Now insert all the cards and do the necessary cabling. Make sure to put on the antistatic bands.

## Slide 4: Standalone Installation and Commissioning Checks
COMMISSIONING
  Steps by BTS HW Configurator
  Run the configuration wizard for standard configuration and then change it according to the required configuration.
  Now install Base band cards, Power supply and transmission cards.
  Send BTS configuration to BTS. It is very important to set the correct cabling in the BTS HW configurator.
  Note down the passive units serial numbers, complete passive units configuration and send to BTS.
  Save the BTS hw configuration file (.hwc) and also passive units configuration file (.hwi)

## Slide 5: Standalone Installation and Commissioning Checks
Ultra Hub Manager
Check/write the identifications of the card.
LIF setting, CRC settings for FXC E1 cards
Make sure to disable all unused LIFs
Configuration settings
Check and write the identification name for FXC Units.(Name will be Site ID)
Synchronization settings
Set Priority 1,2,3 clocks
Select the network topology, chain or loop

## Slide 6: Standalone Installation and Commissioning Checks
Traffic Manager
Define the TRX TCH, TRX SIG, OMU SIG and EDAP as per the Abis Plan.
Cross connections
The cross connections for the traffic manager are made automatically. Copy them in the inactive bank.
If the site is in loop, Make sure to reserve the Masking bits for both the directions as per the Transmission/Abis plan.
Bypass all the timeslots/2MBs that are not required for this site.
Now activate the inactive bank
Check the alarms, save the node file.

## Slide 7: Standalone Installation and Commissioning Checks
FINAL STEPS :-
  Download the BTS SW into the ESMA card.
  Now proceed to the commissioning and follow the instructions.
  Checking of external alarms at the time of commissioning. The external alarm cable and the connector have to be verified at the time of commissioning

## Slide 8: Integeration Activities on BTS Site
  Steps 1 - Connecting PCM Cable (Connection between BTS and BSC)
  Step 2- Integration from BSC. Observe the system.

## Slide 9: Integration Activities on BTS Site
Step 1: Connecting Abis cable (10-20 Min)
  Check the loop from DDF at BTS site to FXC Unit.
  Through connect the Transmission path and check the OMUSIG status “WO”with Engineer at BSC/OSS side.
Step 2 : Integration from BSC
  Unlock the BTS site from BSC/OSS.
  Perform the call testing on all the TRXs
    Call testing should be performed using Net Monitor phones.
  GPRS Testing in every Sector
  Check the external alarms are reporting on BSC.
  Make sure that there are no alarms in OSS for this site and BTS Manager Window before leaving the

## Slide 10: Ultrasite internal cabling with out combiner in 1+1+1 and 2+2+2 configuration
1+1+1 without combiner
2+2+2 without combiner

## Slide 11: Ultrasite internal cabling with Triple wide band combiner in 1+1+1 and 2+2+2 configuration
1+1+1 with triple WCGT
2+2+2 with triple WCGT

## Slide 12: Ultrasite internal cabling with Triple wide band combiner in 3+3+3 and 4+4+4 configuration
3+3+3 with triple WCGT
4+4+4 with triple WCGT

## Slide 13: Ultrasite internal cabling with Triple wide band combiner in 6+6+6 configuration
6+6+6 with triple WCGT ( 1st cabinet)
6+6+6 with triple WCGT ( 2nd cabinet)

## Slide 14
BTS Site traffic Manager

## Slide 15
This Traffic manager configuration will be used for all Ultra site configurations

## Slide 18
Software (Site wizard, BTS SW)
BTS software: CX5.0 CD3.0 for Ultrasite
CXM5.0 CD3.0 for Metrosite.
EP1.1 CD 1.0 for Flexiedge BTS.
Site Wizard: Site wizard 5 CD3.5

## Slide 19
THANKS